## Contacts
Participant (Customer) Contact |  | Participant (Customer) Contact
Contact Name |  | Contact Name | Lowell Faucett
Title |  | Title | Oregon State University Architect
Phone |  | Phone | 541-737-5903
Email |  | Email | lowell.fausett@oregonstate.edu
CBEA Contact |  | Participant (Customer) Contact
Contact Name | Suzanne Marinello P.E. | Contact Name | Joshua Price
Title | Lead Energy Analyst Lead Instructor | Title | Hyslop Research Facility Director
Phone | 541-207-8205 | Phone | 971-285-0306
Email | marinellos@lanecc.edu | Email | joshua.price@oregonstate.edu
CBEA Contact |  | CBEA Contact
Contact Name | Jacob Ray Gradwohl | Contact Name | Suzanne Marinello P.E.
Title | Lead Student Intern | Title | Lead Energy Analyst Lead Instructor
Email | gradwoja@oregonstate.edu | Phone | 541-207-8205
CBEA Contact |  | Email | marinellos@lanecc.edu
Contact Name | Yuki Klein | CBEA Contact
Title | Student Intern | Contact Name | Jacob Ray Gradwohl
Email | kleiny@oregonstate.edu | Title | Lead Student Intern
|  | Email | gradwoja@oregonstate.edu
CBEA Contact
|  | Contact Name | Yuki Klein
|  | Title | Student Intern
|  | Email | kleiny@oregonstate.edu

## 2021 Utility
2021 Electrical Data
Month | kWh | kWh Charge | Charge / kWh | kW | kW Charge | Fees
Jan | 9400 | 978 | 0.10404 | 36 | 228 | 110
Feb | 12840 | 1266 | 0.098598 | 40 | 226 | 110
Mar | 10200 | 1068 | 0.10471 | 46 | 228 | 110
Apr | 12720 | 1190 | 0.093553 | 40 | 226 | 110 | Assumed
May | 11360 | 1130 | 0.099472 | 36 | 228 | 110 | Demand Cost = | 5.8961 | per kW
Jun | 12560 | 1188 | 0.094586 | 36 | 226 | 110
Jul | 9280 | 923 | 0.099461 | 36 | 228 | 110
Aug | 7960 | 861 | 0.10817 | 40 | 226 | 110
Sep | 7640 | 837 | 0.10955 | 40 | 228 | 110
Oct | 9960 | 1024 | 0.10281 | 36 | 226 | 110
Nov | 10120 | 1053 | 0.10405 | 40 | 228 | 110
Dec | 10680 | 1108 | 0.10375 | 36 | 226 | 110
TOTALS | 124720 | 12626 | 0.10123 | 462 | 2724 | 1320
2021 Natural Gas Data
Month | Therms | Cost | Cost / Therm | Other Charges | Total
Jan | 223.1 | 178.97 | 0.8022 | 58 | 236.97
Feb | 254.7 | 204.32 | 0.8022 | 16.87 | 221.19
Mar | 66.2 | 53.1 | 0.80211 | 44.45 | 97.55
Apr | 18.9 | 15.16 | 0.80212 | 32.31 | 47.47
May | 9.6 | 7.7 | 0.80208 | 28.04 | 35.74
Jun | 798.4 | 640.47 | 0.80219 | 18.81 | 659.28
Jul | 757 | 607.26 | 0.80219 | 16.05 | 623.31
Aug | 146.9 | 117.84 | 0.80218 | 16.05 | 133.89
Sep | 113.1 | 90.73 | 0.80221 | 16.11 | 106.84
Oct | 255.5 | 204.96 | 0.80219 | 16.79 | 221.75
Nov | 921.5 | 796.26 | 0.86409 | 61.93 | 858.19
Dec | 381.3 | 362.92 | 0.9518 | 55.52 | 418.44
TOTALS | 3946.2 | 3279.69 | 0.8311 | 380.93 | 3660.62

## EEM Summary
EEM Summary Table
Measure Number | Measure Description | Annual Energy and Cost Savings |  |  |  | Measure Cost and Simple Payback
|  | Electricity Savings |  | Gas Fuel Savings | Total Cost Savings | Measure Cost | Simple Payback
|  | kWh | kW | Therms |  |  | Year
EEM 1 | Lighting Upgrade* | 30258 | 10.086 | - | 3122.6296 | 37260 | 11.9323
EEM 2 | Occupancy Sensors | 6750 | - | - | 683.3347 | 3000 | 4.3902
EEM 3 | Building Insulation* | 34860 | - | - | 3529.0439 | 72976 | 20.6787
EEM 4 | Programmable Thermostats | 7500 | - | - | 759.2607 | 2250 | 2.9634
EEM 5 | Premium Efficient Motors* | 604.0403 | - | - | 61.1499 | 300 | 4.906
Totals (Recommended Measures)
|  | 79972.0403 |  | 0 | 8155.4189 | 115786 | 14.1974
* These measures exceed 5 year simple payback. Included in report for Client but not considered for AR.
Capital Improvement | Description | Annual Energy and Cost Savings |  |  | Measure Cost and Simple Payback
|  | Electricity Savings | Gas Fuel Savings | Total Cost Savings | Measure Cost | Simple Payback | Eligible for Utility Incentive
|  | kWh | Therms |  |  | Year
Ventilation | Mechanical Ventilation |  |  |  |  | NA
2021 Totals
124720 | kWh per year | 12626 | Elec Total Cost |  | 0.10123 | Elec Cost/kWh
3946.2 | Therm per year | 3660.62 | NG Total Cost |  | 9.2763 | NG Cost/MBtu
394.62 | Mbtu/yr (NG)
% Savings with EEMs
64.12% | kWh per year
0% | Therms per year

## EEM #1 Lighting Upgrade
EEM #1 Lighting Upgrade
Existing Lighting | [5 empty] | Proposed Lighting |  |  |  | Aprox. Installed Cost Each | Subtotal
Fixture Type | Description | Watt/Fixture | Quantity | Total Watt Fixture Type | Fixture Type | Description | Watt/Fixture | Quantity | Total Watt Fixture Type
A | Surface Wrap with acrylic lens, 4 ft with 2 lamps fluorescent | 60 | 79 | 4740 | L1 | EMS-L48-4000LM-IMAFL-WD-40K-80CRI | 24 | 79 | 1896 | 250 | 19750
B | Industrial - Open lamps with reflector 4 ft long 4 lamps fluorescent | 160 | 10 | 1600 | L2 | EMS-L24-9000LM-PST-MD-40K-80CRI | 59 | 10 | 590 | 250 | 2500
C | Surface Wrap with acrylic lens, 8 ft with 2 lamps fluorescent | 120 | 10 | 1200 | L3 | EMS-L96-9000LM-IMAFL-WD-40K-80CRI | 53 | 10 | 530 | 300 | 3000
D | Industrial strip - Open lamps with reflector 8 ft long with 4 lamps | 120 |  | 0 | L4 | EMS-L96-9000LM-IMAFL-WD-40K-80CRI | 53 |  | 0 | 300 | 0
E | Keyless Incansescent | 60 | 8 | 480 | L5 | LED MEDIUM BASE LAMP | 20 | 8 | 160 | 45 | 360
F | High mount round HAT incansdescent or CFL | 300 | 1 | 300 | L6 | PXLW-10000LM-WD-40K-80CRI-PM | 74 | 1 | 74 | 450 | 450
G | Jelly jar incandescent | 100 | 1 | 100 | L7 | PXLW-5000LM-WD-40K-80CRI-PM | 35 | 1 | 35 | 350 | 350
H | Pendant stem - HAT incandescent | 300 | 6 | 1800 | L8 | PXLW-10000LM-WD-40K-80CRI-PM | 74 | 6 | 444 | 450 | 2700
I | Clasified (explosion proff) jelly jar incandescent | 200 | 4 | 800 | L9 | HRLL-8L-GO-AS-50K-CM | 94 | 4 | 376 | 800 | 3200
J | Industrial strip with specular reflector 4 ft with 2 lamps | 60 | 56 | 3360 | L10 | EMS-L48-4000LM-IMAFL-WD-40K-80CRI | 24 | 56 | 1344 | 220 | 12320
K | Ice cube trap 4 ft 2 lamp T12 fluorescent | 120 | 4 | 480 | L11 | EMS-L48-4000LM-IMAFL-WD-40K-80CRI | 24 | 4 | 96 | 220 | 880
L | Troffer 2 x 4 4 lamp fluorescent | 120 | 2 | 240 | L12 | HVT-2X4-DOP-5500-4OK | 52 | 2 | 104 | 250 | 500
M | Exterior Barn Light | 200 | 4 | 800 | L13 | WLT-F-R3-4K-UA-6K-TB-P3-PCLL | 79 | 4 | 316 | 200 | 800
N | Exterior Small wall pack over man door | 75 | 1 | 75 | L14 | HLWPC2-P10-40K-TFTM | 28 | 1 | 28 | 200 | 200
O | Exterior Wallpack medium front entrance | 175 | 1 | 175 | L15 | HLWPC2-P30-40K-TFTM | 71 | 1 | 71 | 250 | 250
|  |  |  | 16150 |  |  |  |  | 6064 |  | 47260
On Time Hrs
| Total Existing Watt | 16150 | 3000 | 48450 | kWh |  |  |  |  | Potential Utility Rebate | 10000
| Total Proposed Watt | 6064 | 3000 | 18192 | kWh
[10 empty] | Rough estimate installed cost | 37260
| On Time Hrs = | 3000 | hrs
| Demand Savings = | 10.086 | kW | Demand Cost = | 5.8961 | per kW
| kWh Savings = | 30258 | kWh | Elec Cost = | 0.10123 | per kWh
| Elec Demand Cost Savings = | 59.4681
| Elec Cost Savings = | 3063.1615
| Total Savings = | 3122.6296
| Simple Payback | 11.9323 | years |  |  |  | EEM #1 Estimated Savings
[7 empty] | Annual Energy Usage & Savings Estimate |  | Baseline Electric Usage (kWh) |  |  | 48450
[9 empty] | Proposed Electric Usage (kWh) |  |  | 18192
[9 empty] | Electric Savings (kWh) |  |  | 30258
[9 empty] | Electric Cost Savings ($) |  |  | 3063.1615
[9 empty] | Demand Savings (kW) |  |  | 10
[9 empty] | Electric Demand Savings ($) |  |  | 59.4681
[9 empty] | Baseline Natural Gas Usage (Therms) |  |  | -
[9 empty] | Proposed Natural Gas Usage (Therms) |  |  | -
[9 empty] | Natural Gas Savings (Therms) |  |  | -
[9 empty] | Natural Gas Savings ($) |  |  | -
[9 empty] | Annual Energy Cost Savings |  |  | 3122.6296
[7 empty] | Measure Cost & Simple Payback |  | Project Cost |  |  | 37260
[9 empty] | Simple Payback (Cost/Savings) |  |  | 11.9323

## EEM #2 Occupancy Sensors
EEM #2 | Occupancy Sensor in Spaces
Existing Conditions
Rooms do not have Occupancy Sensors
| Fixture Type | Description | Watt/Fixture | Quantity | Total Watt Fixture Type
| A | Surface Wrap with acrylic lens, 4 ft with 2 lamps fluorescent | 60 | 79 | 4740
| B | Industrial - Open lamps with reflector 4 ft long 4 lamps fluorescent | 160 |  | 0
| C | Surface Wrap with acrylic lens, 8 ft with 2 lamps fluorescent | 120 | 10 | 1200
| D | Industrial strip - Open lamps with reflector 8 ft long with 4 lamps | 120 |  | 0
| E | Keyless Incansescent | 60 | 8 | 480
| F | High mount round HAT incansdescent or CFL | 300 | 1 | 300
| G | Jelly jar incandescent | 100 | 1 | 100
| H | Pendant stem - HAT incandescent | 300 | 6 | 1800
| I | Clasified (explosion proff) jelly jar incandescent | 200 | 4 | 800
| J | Industrial strip with specular reflector 4 ft with 2 lamps | 60 | 56 | 3360
| K | Ice cube trap 4 ft 2 lamp T12 fluorescent | 120 | 4 | 480
| L | Troffer 2 x 4 4 lamp fluorescent | 120 | 2 | 240
[5 empty] | 13500 | Watt Existing
| kWh = watts/1000 x ON time hr |  |  |  | 40500 | kWh Existing | Assume On Time at 3000 hrs per year
[5 empty] | 33750 | kWh Proposed | Assume reduce to 2500 hrs per year ON time
Cost
|  | EEM #2 Estimated Savings | [6 empty] | Cost/Sensor = | 150
|  | Annual Energy Usage & Savings Estimate |  | Baseline Electric Usage (kWh) |  |  |  | 40500 | # sensors = | 20 | `
|  |  |  | Proposed Electric Usage (kWh) |  |  |  | 33750 | Estimated Cost = | 3000
|  |  |  | Electric Savings (kWh) |  |  |  | 6750
|  |  |  | Electric Cost Savings ($) |  |  |  | 683.3347 | Simple Payback = | 4.3902
Baseline Natural Gas Usage (Therms)
|  |  |  | Proposed Natural Gas Usage (Therms) |  |  |  | -
|  |  |  | Natural Gas Savings (Therms) |  |  |  | -
|  |  |  | Natural Gas Savings ($) |  |  |  | 0
|  |  |  | Annual Energy Cost Savings |  |  |  | 683.3347
|  | Measure Cost & Simple Payback |  | Project Cost |  |  |  | 3000
|  |  |  | Simple Payback (Cost/Savings) |  |  |  | 4.3902

## EEM #3 Building Insulation
EEM #2 | Building Insulation
Existing Conditions
Approx, 80% of the exterior walls and roof are uninulsted.
Additionally approximately 20 windows are single pane, metal framed and need to be replaced.
eQUEST Building Simulation was used to estimate energy savings by upgrading the building envelope and windows.
|  |  | Baseline Energy = | 135180 | kWh
|  |  | Proposed Energy = | 100320 | kWh
EEM #3 Estimated Savings
|  | Annual Energy Usage & Savings Estimate | Baseline Electric Usage (kWh) |  |  | 135180
|  |  | Proposed Electric Usage (kWh) |  |  | 100320
|  |  | Electric Savings (kWh) |  |  | 34860
|  |  | Electric Cost Savings ($) |  |  | 3529.0439
|  |  | Baseline Natural Gas Usage (Therms) |  |  | -
|  |  | Proposed Natural Gas Usage (Therms) |  |  | -
|  |  | Natural Gas Savings (Therms) |  |  | -
|  |  | Natural Gas Savings ($) |  |  | -
|  |  | Annual Energy Cost Savings |  |  | 3529.0439
|  | Measure Cost & Simple Payback | Project Cost |  |  | 72976
|  |  | Simple Payback (Cost/Savings) |  |  | 20.6787

## EEM #4 Programmable Tstats
EEM #4 | [6 empty] | Calculations
Programmable T'Stats on Elec Wall Heaters
Elec Heater kWh = kW x hrs ON
Elec Cost = | 0.10123 |  | 1500 | hr/year | Hrs ON based on Bin Data and assumption tht units ar on whem t ambient is between 50 - 60 deg F
% Savings = (Existing - Proposed)/Existing
15 Elec Unit Heaters | 5 | kW
Hrs ON Overheating | 1500 | hr
Assume $150 per Thermostat
Oveheating Energy | 7500 | kWh
EEM #4 Estimated Savings
[5 empty] | Electric Savings (kWh) | 7500
[5 empty] | Electric Cost Savings ($) | 759.2607
[5 empty] | Baseline Natural Gas Usage (Therms) | 0
[5 empty] | Proposed Natural Gas Usage (Therms) | 0
[5 empty] | Natural Gas Savings (Therms) | 0
[5 empty] | Natural Gas Savings ($) | 0
[5 empty] | Annual Energy Cost Savings | 759.2607
|  |  | Measure Cost & Simple Payback |  | Project Cost | 2250
[5 empty] | Simple Payback (Cost/Savings) | 2.9634

## EEM #5 Premium Eff Motors
EEM #5 |  |  | Calculations
Premium Efficiency Motors
Power (kW) = HP x .746 kW/HP x Load/efficiency
Elec Cost = | 0.10123 |  | Hrs = | 1200 | hrs run time per year
|  |  | Load = | 75%
Existing Conditions |  |  | efficiency = | 84% | existing
3 Qty 3 HP Motors 84% eff |  |  | efficiency = | 91.7% | Premuim
Energy Use Existing = | 7193.5714 | kWh | Energy Use = Power (kW) x hrs
|  |  | Material Cost = | 100 | per motor
Proposed Conditions
3 Qty 3 HP Motors 91.7% eff | 6589.5311 | kWh
EEM #5 Estimated Savings
|  |  | Annual Energy Usage & Savings Estimate |  | Baseline Electric Usage (kWh) | 7193.5714
[5 empty] | Proposed Electric Usage (kWh) | 6589.5311
[5 empty] | Electric Savings (kWh) | 604.0403
[5 empty] | Electric Cost Savings ($) | 61.1499
[5 empty] | Baseline Natural Gas Usage (Therms) | -
[5 empty] | Proposed Natural Gas Usage (Therms) | -
[5 empty] | Natural Gas Savings (Therms) | -
[5 empty] | Natural Gas Savings ($) | -
[5 empty] | Annual Energy Cost Savings | 61.1499
|  |  | Measure Cost & Simple Payback |  | Project Cost | 300
[5 empty] | Simple Payback (Cost/Savings) | 4.906

## 2021 Natural Gas
Natutal Gas
Date | Gas Usage | Therms Cost | Service Chage | Other Charges
Therms
2021-01-28 | 223.1 | 178.97 | 15 | 8.83 | 1 Therm = | 100,000 Btu
2021-02-26 | 254.7 | 204.32 | 15 | 9.97 | 1 Mbtu = | 1,000,000 Btu
2021-03-29 | 66.2 | 53.1 | 15 | 3.1
2021-04-27 | 18.9 | 15.16 | 15 | 1.38 | 1 Therm = | 10 Mbtu
2021-05-26 | 9.6 | 7.7 | 15 | 1.03
2021-06-25 | 798.4 | 640.47 | 15 | 29.82
2021-07-27 | 757 | 607.26 | 15 | 28.31
2021-08-25 | 146.9 | 117.84 | 15 | 6.05
2021-09-24 | 113.1 | 90.73 | 15 | 4.81
2021-10-25 | 255.5 | 204.96 | 15 | 10.01
2021-11-23 | 540.2 | 433.34 | 8.79 | 36.92
2021-11-23 | 381.3 | 362.92 | 6.21 | 0
2021-12-28 | 315.7 | 300.48 | 15 | 14.35
Total | 3880.6 | 3217.25 | 180 | 154.58
| 388.06 | Mbtu
| 8.2906 | per Mbtu
| 334.58 | Other Charges 2021

## 2021 Electrical
Period | Usage(kwh) | Average Temperature | Billing total
2022-06-01 | 6240 | 62.75 | 726 | Floor Area = | 16513 | sq. ft.
2022-05-01 | 6440 | 54.98 | 756 | 2021 Electrical
2022-04-01 | 8640 | 48.14 | 931 |  | kWh | Cost |  | Annual Electrical
2022-03-01 | 11120 | 49.22 | 1136 | 2021-12-01 | 9400 | 978 |  | 124720 | kWh | 1 kWh = 3414 Btu
2022-02-01 | 11000 | 44.07 | 1167 | 2021-11-01 | 12840 | 1266 |  | 425794.08 | kBtu | 1000 Btu = 1 kBtu
2022-01-01 | 10680 | 42.25 | 1054 | 2021-10-01 | 10200 | 1068
2021-12-01 | 9400 | 42.53 | 978 | 2021-09-01 | 12720 | 1190
2021-11-01 | 12840 | 50.68 | 1266 | 2021-08-01 | 11360 | 1130 | EUI (elec) = | 25.7854 | kBu/sf
2021-10-01 | 10200 | 54.29 | 1068 | 2021-07-01 | 12560 | 1188
2021-09-01 | 12720 | 66.42 | 1190 | 2021-06-01 | 9280 | 923
2021-08-01 | 11360 | 73.45 | 1130 | 2021-05-01 | 7960 | 861
2021-07-01 | 12560 | 72.87 | 1188 | 2021-04-01 | 7640 | 837
2021-06-01 | 9280 | 68.81 | 923 | 2021-03-01 | 9960 | 1024
2021-05-01 | 7960 | 58.6 | 861 | 2021-02-01 | 10120 | 1053
2021-04-01 | 7640 | 52.86 | 837 | 2021-01-01 | 10680 | 1108
2021-03-01 | 9960 | 44.38 | 1024
2021-02-01 | 10120 | 42.71 | 1053 |  | 124720 | 12626
2021-01-01 | 10680 | 43.32 | 1108
2020-12-01 | 10560 | 42.43 | 1149 |  | Cost/kWh = | 0.10123
2020-11-01 | 11600 | 45.01 | 1170
2020-10-01 | 7560 | 55.57 | 845
2020-09-01 | 6400 | 65.03 | 760
2020-08-01 | 8400 | 70.26 | 895
2020-07-01 | 9640 | 67.59 | 1011
2020-06-01 | 7600 | 61.84 | 857