## Contacts
Use this Contact for DOE Report |  | Use this contact for Client Report
Participant (Customer) Contact |  | Participant (Customer) Contact
Contact Name |  | Contact Name | Jen Brown
Title |  | Title | Sustainablilty Coordinator Benton County
Phone |  | Phone | 541-766-6110
Email |  | Email | jennifer.brown@co.benton.or.us
CBEA Contact |  | Participant (Customer) Contact
Contact Name | Suzanne Marinello P.E. | Contact Name | Paul Wallsinger
Title | Lead Energy Analyst Lead Instructor | Title | Facilities Manager
Phone | 541-207-8205 | Phone | 541-766-6821
Email | marinellos@lanecc.edu | Email | Paul.Walklsinger@Co.Benton.OR.US
CBEA Contact |  | CBEA Contact
Contact Name | Jacob Ray Gradwohl | Contact Name | Suzanne Marinello P.E.
Title | Lead Student Intern | Title | Lead Energy Analyst Lead Instructor
Email | gradwoja@oregonstate.edu | Phone | 541-207-8205
CBEA Contact |  | Email | marinellos@lanecc.edu
Contact Name | Yuki Klein | CBEA Contact
Title | Student Intern | Contact Name | Jacob Ray Gradwohl
Email | kleiny@oregonstate.edu | Title | Student Intern
|  | Email | gradwoja@oregonstate.edu
CBEA Contact
|  | Contact Name | Yuki Klein
|  | Title | Student Intern
|  | Email | kleiny@oregonstate.edu

## Historic Energy Use
The tables on this sheet corresponds to the 3-year-average of energy usage for each month. | [7 empty] | USE THIS TABLE FOR TABLE 2 HISTORICAL ENERGY USE
|  | Electricity |  | Natural Gas |  | Electricity | Natural Gas |  |  | Electrical Use (kWh) |  |  |  | Natural Gas Use (Therms)
|  | kWh | kW | Therms |  | kBtu |  | Month | 2019 | 2020 | 2021 | 3-year Ave. | 2019 | 2020 | 2021 | 3-Year Ave.
| January | 0 |  | 0 | January | 0 | 0 | January |  |  |  | 0 |  |  |  | 0
| February | 0 |  | 0 | February | 0 | 0 | February |  |  |  | 0 |  |  |  | 0
| March | 0 |  | 0 | March | 0 | 0 | March |  |  |  | 0 |  |  |  | 0
| April | 0 |  | 0 | April | 0 | 0 | April |  |  |  | 0 |  |  |  | 0
| May | 0 |  | 0 | May | 0 | 0 | May |  |  |  | 0 |  |  |  | 0
| June | 0 |  | 0 | June | 0 | 0 | June |  |  |  | 0 |  |  |  | 0
| July | 0 |  | 0 | July | 0 | 0 | July |  |  |  | 0 |  |  |  | 0
| August | 0 |  | 0 | August | 0 | 0 | August |  |  |  | 0 |  |  |  | 0
| September | 0 |  | 0 | September | 0 | 0 | September |  |  |  | 0 |  |  |  | 0
| October | 0 |  | 0 | October | 0 | 0 | October |  |  |  | 0 |  |  |  | 0
| November | 0 |  | 0 | November | 0 | 0 | November |  |  |  | 0 |  |  |  | 0
| December | 0 |  | 0 | December | 0 | 0 | December |  |  |  | 0 |  |  |  | 0
Annual Energy Usage
[5 empty] | Total kBtu | 0 |  | Annual Elec Energy Usage (kWh) |  |  |  | 0
[5 empty] | SF | 124000 |  | Annual NG Energy Usage (Therms) |  |  |  |  | 0 | 0 | 0 | 0
[5 empty] | EUI | 0 |  | Annual Elec Energy kBtu | 0 | 0 | 0 | 0
[5 empty] | Median EUI | 65.7 |  | Annual NG Energy Usage kBtu | 0 | 0 | 0 | 0
[8 empty] | Total Annual Energy Usage (MMBtu) | 0 | 0 | 0 | 0
Energy Performace of the Facility
|  | UDATE CHARTS WITH CURRENT SITE DATA | [5 empty] | Conditioned Space Area (sqft)
[8 empty] | Total Energy Use (MMBtu per year, 3-year ave.) | [5 empty] | 0
[8 empty] | Energy Use Intensity, EUI (kBtu/sqft/year) | [5 empty] | #VALUE!
*Median EUI for Facility Type in the US
Elec Energy Use in kBtu = Annual kWh x 3414 Btu/kWh / 1000
NG Energy Use in Btu = Therms/100,000
NG Energy Use in kBtu = Btu/1000
! MMBtu = 1000 kBtu

## 2021Energy Cost Analysis
USE THESE TABLES FOR SECTION 5 ENERGY COST ANALYSIS TABLE 1 YEAR 2021 UTIITY DATA
2021 Electrical Data
Month | kWh | kWh Charge | Charge / kWh | kW | kW Charge | Fees
Jan | 35040 | 2035.46 | 0.05809 | 126 | 881.31 | 506.37
Feb | 32640 | 1886.42 | 0.05809 | 124 | 866.59 | 476.3
Mar | 32640 | 1886.42 | 0.05809 | 119 | 833.64 | 474.96
Apr | 26640 | 1552.63 | 0.05809 | 111 | 787.96 | 393.1
May | 21120 | 1239.81 | 0.05809 | 62 | 508.17 | 306.78 | Demand Cost = | 7.2786 | per kW
Jun | 22320 | 1308.39 | 0.05809 | 66 | 531.01 | 539.3
Jul | 25680 | 1500.41 | 0.05809 | 84 | 633.79 | 373.42
Aug | 5993 | 352.33 | 0.05809 | 36 | 268.41 | 92.7
Sep | 24240 | 1418.49 | 0.05809 | 74 | 576.69 | 351.61
Oct | 22080 | 1297.32 | 0.05809 | 72 | 565.27 | 322.33
Nov | 30720 | 1795.25 | 0.05809 | 128 | 885.58 | 452.49
Dec | 41040 | 2388.54 | 0.05809 | 125 | 864.6 | 589.65
TOTALS | 320153 | 18661.47 | 0.058289 | 1127 | 8203.02 | 4879.01
2021 Natural Gas Data
Month | Therms | Cost | Cost / Therm | Other Charges | Total
Jan | 549 | 432.1 | 0.78707 | 48.99 | 481.09
Feb | 863.9 | 487.36 | 0.78707 | 58.01 | 545.37
Mar | 656.3 | 514.01 | 0.78707 | 18.56 | 532.57
Apr | 494.3 | 390.11 | 0.78707 | 41.53 | 964.21
May | 397.8 | 300.51 | 0.78707 | 35.66 | 336.17
Jun | 150.4 | 148.82 | 0.78707 | 25.73 | 174.55
Jul | 109.8 | 88.08 | 0.78707 | 25.24 | 113.32
Aug | 5.6 | 4.49 | 0.78707 | 16.28 | 20.77
Sep | 1.1 | 0.88 | 0.78707 | 16.04 | 16.92
Oct | 0 | 0 | 0.78707 | 15.99 | 15.99
Nov | 1.1 | 0.88 | 0.78707 | 16.04 | 16.92
Dec | 326.7 | 282.41 | 0.78707 | 34.48 | 316.89
TOTALS | 3556 | 2649.65 |  | 352.55 | 3534.77
| Total MMBtu = | 355.6
| Unit Cost = | 9.9403 | $/MMBtu

## EEM Summary
Insert this Table into Report "EEM Cost Estimates"
EEM Summary Table
Measure Number | Measure Description | Annual Energy and Cost Savings |  |  |  | Measure Cost and Simple Payback
|  | Electricity Savings |  | Gas Fuel Savings | Total Cost Savings | Measure Cost | Simple Payback
|  | kWh | kW | Therms |  |  | Year
EEM 1 | Lighting Upgrade | 94957.72 | 28.094 | - | 5739.4978 | 21350 | 3.7198
EEM 2 | Occupancy Sensors | 32364.8 | - | - | 1886.5191 | 2000 | 1.0602
EEM 3 | Upgrade Controls | 324010 | - | - | 1949.1917 | 15000 | 7.6955
Totals
|  | 451332.52 |  | 0 | 9575.2085 | 38350 | 4.0051
Capital Improvement | Description | Annual Energy and Cost Savings |  |  |  | Measure Cost and Simple Payback
|  | Electricity Savings |  | Gas Fuel Savings | Total Cost Savings | Measure Cost | Simple Payback
|  | kWh | kW | Therms |  |  | Year
EEM 4 | Economzer Control on Upper Level | 7310 | - | - | 426.0942 | 10000 | 23.469
2021 Totals
320153 | kWh per year | 18661.47 | Elec Total Cost |  | 0.058289 | Elec Cost/kWh
1127 | kW Elec Demand | 8203.02 | Demand Cost |  | 7.2786 | Demand Cost
| Elec Fees | 4879.01
3556 | Btu per year Therms
355.6 | MMbtu/yr Therms | 3534.77 |  |  | 9.9403 | NG Cost/MBtu

## EEM #1 Lighting Upgrade
EEM #1 Lighting Upgrade
| Electrical Cost = | 0.058289 | per kWh
| Demand Cost = | 7.2786 | per kW
Existing Conditions
| Fixture Type | lamps per Fixtrure | Wall/lamp | Watt/fixture | Qty | Total Watt
| 4' T8 | 2 | 32 | 64 | 389 | 24896
| 8' T8 | 2 | 59 | 118 | 14 | 1652
| 4' T12 | 2 | 60 | 120 | 1 | 120
| 8' T12 | 2 | 75 | 150 | 23 | 3450
[5 empty] | 427 | 30118 | Watt Existing
Recommended Change
| 4' LED | 2 | 15 | 30 | 389 | 11670
| 8' LED | 2 | 44 | 88 | 14 | 1232
| 4' LED | 2 | 15 | 30 | 1 | 30
| 8' LED | 2 | 44 | 88 | 23 | 2024 | Watt Proposed
| Hours "ON" | 3380 | hrs
Calculations
| Existing Energy = | 101798.84 | kWh |  | Energy (kWh) = Lighting Fixture Watt X No. of Fixture x "ON Hrs
| Existing Energy Cost = | 5933.7754
Demand (kW) = Lighting total Watt/1000
| Proposed Energy = | 6841.12 | kWh
| Proposed Energy Cost = | 398.7636
[5 empty] | Estimated Cost/Fixture = |  | $20/tube
| Existing Demand = | 30.118 |  |  | Installation |  | $30/Fixture
| Existing Demand Cost = | 219.2179
| Proposed Demand = | 2.024 |  |  | Total Count = | 427
| Proposed Demand Cost = | 14.732 |  |  | Total Cost = | 21350
| Demand Savings = | 28.094 | kW
| kWh Savings = | 94957.72 | kWh
| Elec Demand Cost Savings = | 204.4859
| Elec Cost Savings = | 5535.0118
| Total Savings = | 5739.4978
EEM #1 Estimated Savings
[7 empty] | Annual Energy Usage & Savings Estimate | Baseline Electric Usage (kWh) | 101798.84
[8 empty] | Proposed Electric Usage (kWh) | 6841.12
[8 empty] | Electric Savings (kWh) | 94957.72
[8 empty] | Electric Cost Savings ($) | 5535.0118
[8 empty] | Demand Savings (kW) | 28.094
[8 empty] | Electric Demand Savings ($) | 204.4859
[8 empty] | Baseline Natural Gas Usage (Therms) | -
[8 empty] | Proposed Natural Gas Usage (Therms) | -
[8 empty] | Natural Gas Savings (Therms) | -
[8 empty] | Natural Gas Savings ($) | -
[8 empty] | Annual Energy Cost Savings | 5739.4978
[7 empty] | Measure Cost & Simple Payback | Project Cost | 21350
[8 empty] | Simple Payback (Cost/Savings) | 3.7198

## EEM #2 Occupancy Sensors
EEM #2 | Occupancy Sensor in Spaces
| Electrical Cost = | 0.058289 | per kWh
Existing Conditions
Offices do not have Occupancy Sensors
| Fixture Type | Description | Watt/Fixture | Quantity | Total Watt Fixture Type
| General Offices | 4' T8 | 64 | 389 | 24896
| "ON" Time Existing= | 3380 | hrs |  |  |  | Calculations
| Proposed reduces "ON" Time from 10 hrs/day 5 days per week to 8 hrs/day |  |  |  |  | Energy (kWh) = Lighting Fixture Watt X No. of Fixture x "ON Hrs
| "ON" Time proposed = | 2080 | hrs
| Existing Energy = | 84148.48 | kWh
| Existing Energy Cost = | 4904.9496 |  |  |  | Estimated Cost/Sensor = | 50
| Proposed Energy = | 51783.68 | kWh
| Proposed Energy Cost = | 3018.4305 |  |  |  | Total Sensors = | 40
[6 empty] | Total Cost = | 2000
EEM #2 Estimated Savings
|  | Annual Energy Usage & Savings Estimate |  | Baseline Electric Usage (kWh) |  |  |  | 84148.48 | `
|  |  |  | Proposed Electric Usage (kWh) |  |  |  | 51783.68
|  |  |  | Electric Savings (kWh) |  |  |  | 32364.8
|  |  |  | Electric Cost Savings ($) |  |  |  | 1886.5191
Baseline Natural Gas Usage (Therms)
|  |  |  | Proposed Natural Gas Usage (Therms) |  |  |  | -
|  |  |  | Natural Gas Savings (Therms) |  |  |  | -
|  |  |  | Natural Gas Savings ($) |  |  |  | 0
|  |  |  | Annual Energy Cost Savings |  |  |  | 1886.5191
|  | Measure Cost & Simple Payback |  | Project Cost |  |  |  | 2000
|  |  |  | Simple Payback (Cost/Savings) |  |  |  | 1.0602
1500

## EEM #3 Upgrade Controls
Baseline Energy
EEM #3
Calculations |  |  |  | Proposed:
DDC Control
Elec Cost = | 0.058289 |  |  | Assumes controls will provide
Baseline Energy Use = | 324010 | kWh |  | closer scheduling of equipment
Proposed Energy Use = | 290570 | kWh
Energy Savings = | 33440 | kWh |  | New Contols | 15000
Energy Cost Savings = | 1949.1917
EEM #3 Estimated Savings
|  |  | Electric Savings (kWh) |  |  | 324010
|  |  | Electric Cost Savings ($) |  |  | 1949.1917
|  |  | Baseline Natural Gas Usage (Therms) |  |  | 0
|  |  | Proposed Natural Gas Usage (Therms) |  |  | 0
|  |  | Natural Gas Savings (Therms) |  |  | 0
|  |  | Natural Gas Savings ($) |  |  | 0
|  |  | Annual Energy Cost Savings |  |  | 1949.1917
| Measure Cost & Simple Payback |  | Project Cost |  |  | 15000
|  |  | Simple Payback (Cost/Savings) |  |  | 7.6955
Enhanced Control Energy

## EEM #4 Econimzer on UpperUnits
Baseline Energy
EEM # 4
Calculations |  |  |  | Proposed: Add Econimzer Control to Upper Level Units
Elec Cost = | 0.058289
Baseline Energy Use = | 324010 | kWh
Proposed Energy Use = | 316700 | kWh
Energy Savings = | 7310 | kWh |  |  | 5000
Energy Cost Savings = | 426.0942 |  |  | 5 Units @ $2000 each
EEM #4 Estimated Savings
|  |  | Electric Savings (kWh) |  |  | 7310
|  |  | Electric Cost Savings ($) |  |  | 426.0942
|  |  | Baseline Natural Gas Usage (Therms) |  |  | 0
|  |  | Proposed Natural Gas Usage (Therms) |  |  | 0
|  |  | Natural Gas Savings (Therms) |  |  | 0
|  |  | Natural Gas Savings ($) |  |  | 0
|  |  | Annual Energy Cost Savings |  |  | 426.0942
| Measure Cost & Simple Payback |  | Project Cost |  |  | 10000
|  |  | Simple Payback (Cost/Savings) |  |  | 23.469
Control Economizer on Upper Floor Units