## Contacts
Use this Contact for DOE Report |  | Use this contact for Client Report
Participant (Customer) Contact |  | Participant (Customer) Contact
Contact Name |  | Contact Name | Jen Brown
Title |  | Title | Sustainablilty Coordinator Benton County
Phone |  | Phone | 541-766-6110
Email |  | Email | jennifer.brown@co.benton.or.us
CBEA Contact |  | Participant (Customer) Contact
Contact Name | Suzanne Marinello P.E. | Contact Name | Paul Wallsinger
Title | Lead Energy Analyst Lead Instructor | Title | Facilities Manager
Phone | 541-207-8205 | Phone | 541-766-6821
Email | marinellos@lanecc.edu | Email | Paul.Walklsinger@Co.Benton.OR.US
CBEA Contact |  | CBEA Contact
Contact Name | Jacob Ray Gradwohl | Contact Name | Suzanne Marinello P.E.
Title | Lead Student Intern | Title | Lead Energy Analyst Lead Instructor
Email | gradwoja@oregonstate.edu | Phone | 541-207-8205
CBEA Contact |  | Email | marinellos@lanecc.edu
Contact Name | Yuki Klein | CBEA Contact
Title | Student Intern | Contact Name | Jacob Ray Gradwohl
Email | kleiny@oregonstate.edu | Title | Lead Student Intern
|  | Email | gradwoja@oregonstate.edu
CBEA Contact
|  | Contact Name | Yuki Klein
|  | Title | Student Intern
|  | Email | kleiny@oregonstate.edu

## Energy Data
Insert this Table into Report under "Energy Cost Analysis" 2021 Energy Use
2021 Electrical Data
Month | kWh | kWh Charge | Charge/kWh | kW | kW Charge | Other Charges | Fees
January | 1955 | 176.341 | 0.0902 | 21.5 | 1.9393 | 25.66 | 203.9403
February | 2265 | 204.303 | 0.0902 | 21.39 | 1.9294 | 25.7 | 231.9324
March | 2331 | 210.2562 | 0.0902 | 17.26 | 1.5569 | 25.74 | 237.5531
April | 1843 | 166.2386 | 0.0902 | 20.75 | 1.8717 | 25.76 | 193.8702
May | 1500 | 135.3 | 0.0902 | 16.89 | 1.5235 | 25.7 | 162.5235
June | 955 | 86.141 | 0.0902 | 20.53 | 1.8518 | 25.86 | 113.8528
July | 1068 | 96.3336 | 0.0902 | 20.53 | 1.8518 | 25.67 | 123.8554
August | 1106 | 99.7612 | 0.0902 | 10.19 | 0.91914 | 25.24 | 125.9203
September | 1706 | 153.8812 | 0.0902 | 9.43 | 0.85059 | 25.12 | 179.8518
October | 1268 | 114.3736 | 0.0902 | 11.01 | 0.9931 | 30.34 | 145.7067
November | 994 | 89.6588 | 0.0902 | 16.34 | 1.4739 | 30.55 | 121.6827
December | 1124 | 101.3848 | 0.0902 | 23.27 | 2.099 | 30.59 | 134.0738
TOTALS | 18115 | 1633.973 | 0.0902 | 209.09 | 18.8599 | 321.93 | 1974.7629
In additional to electrical use, the facility purchased 81.64 gallons propane for 2021
Total Btu Electricity | 61844610 | Btu
Total Btu Propane | 7470060 | Btu |  | Propane Fuel Density = | 91500 | Btu/gallon |  | 7470.06
Total Energy | 69314670 | Btu | [5 empty] | 747.006
KBtu/sqft | 32.4507 | kBtu/sf EUI
Floor Area = | 2136 | sq. ft
Gallons Propane 2021 | 81.64 | Gallons Propane
| 7470060 | Btu Propane
| 747.006 | MMBtu Propane
| 209.46 | Propane Cost for 2021
747

## EEM Summary
Insert this Table into Report "EEM Cost Estimates"
EEM Summary Table
Measure Number | Measure Description | Annual Energy and Cost Savings |  |  |  | Measure Cost and Simple Payback
|  | Electricity Savings |  | Gas Fuel Savings | Total Cost Savings | Measure Cost | Simple Payback
|  | kWh | kW | Therms |  |  | Year
EEM 1 | Lighting Upgrade | 1393.6 | 0.536 | - | 125.7511 | 390 | 3.1014
EEM 2 | Occupancy Sensors | 1408 | - | - | 127.0016 | 240 | 1.8897
EEM 3 | Smart Thermostat | 7870 | - | - | 709.874 | 1200 | 1.6904
EEM 4 | New Existing Heat Pump | 8580 | - | - | 773.916 | 15000 | 19.3819
Totals (Recommended Measures)
|  | 19251.6 |  | 0 | 1736.5427 | 16830 | 9.6917
2021 Totals
18115 | kWh per year | 1633.973 | Elec Total Cost |  | 0.0902 | Elec Cost/kWh
7470060 | Btu per year Propane | 209.46 | Propane Total Cost |  | 0.2804 | NG Cost/MBtu
747.006 | MMbtu/yr (Propane)

## EEM #1 Lighting Upgrade
EEM #1 Lighting Upgrade
| Electrical Cost = | 0.0902 | per kWh
| Demand Cost = | 0.0902 | per kW
Existing Conditions
| Fixture Type | lamps per Fixtrure | Wall/lamp | Watt/fixture | Qty | Total
| Type "A" Fixture (T8 4 ft) | 2 | 32 | 64 | 6 | 384
| Type "B" Fixture (T8 4 ft) | 3 | 32 | 96 | 7 | 672
[6 empty] | 1056 | Watt Existing
Recommended Change
| Replace with LED 2 (150 watt/fixture) | 1 | 40 | 40 | 13 | 520 | Watt Recommended
| Hours "ON" | 2600 | hrs
Calculations
| Existing Energy = | 2745.6 | kWh |  |  |  | Energy (kWh) = Lighting Fixture Watt X No. of Fixture x "ON Hrs
| Existing Energy Cost = | 247.6531
Demand (kW) = Lighting total Watt/1000
| Proposed Energy = | 1352 | kWh
| Proposed Energy Cost = | 121.9504
[7 empty] | Estimated Cost/Fixture = | $10/tube
| Existing Demand = | 1.056 |  |  |  |  | Installation | $20/Fixture
| Existing Demand Cost = | 0.09504
| Proposed Demand = | 0.52 |  |  |  |  | Total Fixtures = | 13
| Proposed Demand Cost = | 0.046904 |  |  |  |  | Total Cost = | 390
| Demand Savings = | 0.536 | kW
| kWh Savings = | 1393.6 | kWh
| Elec Demand Cost Savings = | 0.048347
| Elec Cost Savings = | 125.7027
| Total Savings = | 125.7511
EEM #1 Estimated Savings
[7 empty] | Annual Energy Usage & Savings Estimate | Baseline Electric Usage (kWh) | 2745.6
[8 empty] | Proposed Electric Usage (kWh) | 1352
[8 empty] | Electric Savings (kWh) | 1393.6
[8 empty] | Electric Cost Savings ($) | 125.7027
[8 empty] | Demand Savings (kW) | 0.536
[8 empty] | Electric Demand Savings ($) | 0.048347
[8 empty] | Baseline Natural Gas Usage (Therms) | -
[8 empty] | Proposed Natural Gas Usage (Therms) | -
[8 empty] | Natural Gas Savings (Therms) | -
[8 empty] | Natural Gas Savings ($) | -
[8 empty] | Annual Energy Cost Savings | 125.7511
[7 empty] | Measure Cost & Simple Payback | Project Cost | 390
[8 empty] | Simple Payback (Cost/Savings) | 3.1014

## EEM #2 Occupancy Sensors
EEM #2 | Occupancy Sensor in Spaces
| Electrical Cost = | 0.0902 | per kWh
Existing Conditions
Rooms do not have Occupancy Sensors
| Fixture Type | Description | Watt/Fixture | Quantity | Total Watt Fixture Type
| Type "A" | T8 4 ft 2 lamp | 64 | 6 | 384
| Type "B" | T8 4 ft 4 lamp | 128 | 7 | 896
[5 empty] | 1280 | Watt
| "ON" Time Existing= | 2600 | hrs |  |  |  | Calculations
| Proposed reduces "ON" Time from 10 hrs/day 5 days per week to 3 days per week | [5 empty] | Energy (kWh) = Lighting Fixture Watt X No. of Fixture x "ON Hrs
| "ON" Time proposed = | 1500 | hrs
| Existing Energy = | 3328 | kWh
| Existing Energy Cost = | 300.1856 |  |  |  |  | Estimated Cost/Sensor = |  | 50
| Proposed Energy = | 1920 | kWh
| Proposed Energy Cost = | 173.184 |  |  |  |  | Total Sensors = |  | 8
[7 empty] | Total Cost = |  | 240
EEM #2 Estimated Savings
|  | Annual Energy Usage & Savings Estimate |  | Baseline Electric Usage (kWh) |  |  |  | 3328 |  | `
|  |  |  | Proposed Electric Usage (kWh) |  |  |  | 1920
|  |  |  | Electric Savings (kWh) |  |  |  | 1408
|  |  |  | Electric Cost Savings ($) |  |  |  | 127.0016
Baseline Natural Gas Usage (Therms)
|  |  |  | Proposed Natural Gas Usage (Therms) |  |  |  | -
|  |  |  | Natural Gas Savings (Therms) |  |  |  | -
|  |  |  | Natural Gas Savings ($) |  |  |  | 0
|  |  |  | Annual Energy Cost Savings |  |  |  | 127.0016
|  | Measure Cost & Simple Payback |  | Project Cost |  |  |  | 240
|  |  |  | Simple Payback (Cost/Savings) |  |  |  | 1.8897
1500

## EEM #3 Upgrade Controls
EEM #3
Calculations |  |  |  | Proposed: Turn units off on Wednesday and Fridays
Reduce unoccupied heating temp from 65 deg F to 60 deg F
Elec Cost = | 0.0902
Baseline Energy Use = | 22810 | kWh
Proposed Energy Use = | 14940 | kWh
Energy Savings = | 7870 | kWh |  | New Thermostat = | 1200
Energy Cost Savings = | 709.874
EEM #3 Estimated Savings
|  |  | Electric Savings (kWh) |  |  | 7870
|  |  | Electric Cost Savings ($) |  |  | 709.874
|  |  | Baseline Natural Gas Usage (Therms) |  |  | 0
|  |  | Proposed Natural Gas Usage (Therms) |  |  | 0
|  |  | Natural Gas Savings (Therms) |  |  | 0
|  |  | Natural Gas Savings ($) |  |  | 0
|  |  | Annual Energy Cost Savings |  |  | 709.874
| Measure Cost & Simple Payback |  | Project Cost |  |  | 1200
|  |  | Simple Payback (Cost/Savings) |  |  | 1.6904

## EEM #4 New Heat Pump
EEM # 4
Calculations |  |  |  | Proposed: High Efficiency Heat Pump with Economizer
Elec Cost = | 0.0902
Baseline Energy Use = | 22810 | kWh
Proposed Energy Use = | 14230 | kWh
Energy Savings = | 8580 | kWh |  | New Heat Pump = | 15000
Energy Cost Savings = | 773.916
EEM #4 Estimated Savings
|  |  | Electric Savings (kWh) |  |  | 8580
|  |  | Electric Cost Savings ($) |  |  | 773.916
|  |  | Baseline Natural Gas Usage (Therms) |  |  | 0
|  |  | Proposed Natural Gas Usage (Therms) |  |  | 0
|  |  | Natural Gas Savings (Therms) |  |  | 0
|  |  | Natural Gas Savings ($) |  |  | 0
|  |  | Annual Energy Cost Savings |  |  | 773.916
| Measure Cost & Simple Payback |  | Project Cost |  |  | 15000
|  |  | Simple Payback (Cost/Savings) |  |  | 19.3819